## Full Working Sheet
Configuration | Transformer | Column1 | Column2 | Column3 | Approved Manufacturer | Column4 | Approved Manufacturer5 | Column6 | Approved Manufacturer7 | Column8 | Approved Manufacturer9 | Column10 | Approved Manufacturer11 | Column12 | Approved Manufacturer13 | Column14 | Approved Manufacturer15 | Column16 | Approved Manufacturer16 | Substitution Status | Substitution Status2 | Specific Vendor Requirements | Specific Vendor Requirements2 | Specific Vendor Requirements3 | Column20
Configuration | Type: | Size | Primary Component | Category | Manufacturer | Model # | Manufacturer | Model # | Manufacturer | Model # | Manufacturer | Model # | Manufacturer | Model # | Manufacturer | Model # | Manufacturer | Model # |  | Short Term Only | Long Term | Performance | Quality | Other | Aftermarket Option
Minimal (M), Standard (S), Custom © | OH, 1Ph, etc. | kVA | Fuse, Sticker, MOV | Protection, Marking | [15 empty] | Only to expedite | Completely interchangeble | Critical matching requirements | Test specs or other metrics |  | Ability to add at Utility
| 1 Phase Pad | All kva | Transformer Tank Bronze Ground Clamps |  | H-J Enterprises, Inc. |  | Kearney |  | Penn Union | [11 empty] | Completely interchangeble |  |  |  | No
| 1 Phase Pad | All kva | Pressure Relief Valves |  | Qualitrol |  | Beta |  | Heartland | [11 empty] | Completely interchangeble |  |  |  | No
| 1 Phase Pad | All kva | Bushing Wells 125kV BIL | HV Bushing | Elastimold |  | ERMCO |  |  |  | Central Moloney |  | Cooper | [7 empty] | Completely interchangeble |  |  |  | No
| 1 Phase Pad | All kva | Bushing Wells 150kV BIL | HV Bushing | Elastimold |  | Central Moloney |  | Howard | [5 empty] | Hitachi Energy | Universal 200 amp Bushing Wells 95-150 kV BIL with fixed or removable stud see attached component product guide |  |  |  |  | Completely interchangeble |  |  |  | No
| 1 Phase Pad | All kva | Bay-o-net assembly | Protection | Cooper | [9 empty] | Hitachi Energy | DO-III Fuse holder - See attached component product guide |  |  |  |  | Completely interchangeble |  |  |  | No
| 1 Phase Pad | All kva | Boy-o-net fuse holders | Protection | Cooper | [9 empty] | Hitachi Energy | DO-III Fuse holder - See attached component product guide |  |  |  |  | Completely interchangeble |  |  |  | No
| 1 Phase Pad | All kva | Bay-o-net oil drip shields | Protection | Central Moloney |  | Howard |  | RTE (Cooper) |  |  |  | ERMCO |  | Hitachi Energy | DO-III Fuse holder - See attached component product guide |  |  |  |  | Completely interchangeble |  |  |  | No
| 1 Phase Pad | All kva | Low Voltage/Neutral Bushings | LV Bushing | Cooper |  | Central Moloney |  |  |  | Howard |  | H-J Enterprises |  | Hitachi Energy | LV stud bushing family .625-1.25" diamater see attached component product guide |  |  |  |  | Completely interchangeble |  |  |  | Yes
| 1 Phase Pad | All kva | Fiber Optic Oil Level Indicator (19.9kV units) |  | Trayer |  | Heartland | [13 empty] | Completely interchangeble |  |  |  | No
| 1 Phase Pad | All kva | Non-PCB Label |  | Almetek |  | LEM | [13 empty] | Completely interchangeble |  |  |  | No
| 1 Phase Pad | All kva | Bay-o-net Fuse |  | ERMCO |  | Cooper | [7 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble |  |  |  | No
| 1 Phase Pad | All kva | Current Limiting Fuse |  | Cooper |  | GE/Mersen |  | Hi-Tech | [11 empty] | Completely interchangeble |  |  |  | No
| 1 Phase Pad |  | Magnex | Protection | Cooper | MX1AE1SYE03 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex | Protection | Cooper | MX1AE1SYE06 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex | Protection | Cooper | MX1AE1SYE10 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex | Protection | Cooper | MX1AE1SYE12 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex | Protection | Cooper | MX1AE1SYE18 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex | Protection | Cooper | MX1AE1SYE25 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex | Protection | Cooper | MX1AE1SYE30 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC08030C100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC08040C100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC08050C100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC08065C100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC08100C100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC08125C100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC08150D100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Sticker | Marking | Almetek | 17261 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Sticker | Marking | Almetek | 17262 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C04 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 1 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C10 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 1 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C12 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 1 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C14 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 1 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C17 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC08080C100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC08165D100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C06 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 1 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C08 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC23030C100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC23050C100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | ELSP | Protection | Cooper | CBUC23080C100 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex Hardware Kit | Protection | Cooper | 3638535A08 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex Shunt Kit | Protection | Cooper | MXDV125 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex Shunt Kit | Protection | Cooper | MXDV035 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex Shunt Kit | Protection | Cooper | MXDV014 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex Shunt Kit | Protection | Cooper | MXDV0919 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex Shunt Kit | Protection | Cooper | MXDV0256 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex Shunt Kit | Protection | Cooper | MXDV0108 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex Shunt Kit | Protection | Cooper | MXDV0102 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex Shunt Kit | Protection | Cooper | MXDV0029 | [14 empty] | Completely interchangeble
| 1 Phase Pad |  | Magnex Shunt Kit | Protection | Cooper | MXDV0025 | [14 empty] | Completely interchangeble
| 1 Phase Pad | All | Secondary Terminations | Connectors | HOMAC | Z3035 USLRSW Z3035 USL | [13 empty] | Any Zbar type set-screw | Any Zbar type set-screw | Similar build/installation | Verification of being equal |  | Yes
| 1 Phase Pad | All | Primary Bushing Wells | HV Bushing | Eaton | BW150R | Eaton | 2638372C02R | Howard | [5 empty] | Hitachi Energy | Universal 200 amp Bushing Wells 95-150 kV BIL with fixed or removable stud see attached component product guide |  |  |  | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 1 Phase Pad | All | Primary Bushing Wells | Clamp Busing Well | Eaton | 2085399A01 | Kuhlman | 4210212-006 | Howard |  |  |  | Ningbo/Elliot | 4093B89H02 | [5 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 1 Phase Pad | All | Bushing Inserts | Inserts | Elastimold | 1601A4 | Eaton | LBI215 | Hubbell | 9U02AAB001 | [9 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| 1 Phase Pad | All | Bushing Inserts | Inserts | Elastimold |  | Eaton |  | Hubbell
| 1 Phase Pad | All | Fuse Cartridge | Bayonet Fuse | Eaton | 3437922B02M | [13 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 1 Phase Pad | All | Fuse Cartridge | Bayonet Fuse | Eaton | [9 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide
| 1 Phase Pad | All | Dielectric Fluid | Ester Fluids | Cargil | FR3 | Midel | 1215 | [11 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 1 Phase Pad | All | Tank Grounding | Grounds | Penn Union | LSN-050NEJAM | [13 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| 1 Phase Pad | All | Protective Links | Protection | [10 empty] | Hitachi Energy | See product Guide - Protective links
| 1 Phase Pad | All | Tap Changer 5-position | Switch | Howard | [9 empty] | Hitachi Energy | D series https://www.hitachienergy.com/us/en/products-and-solutions/transformer/tap-changers/de-energized-tap-changers-and-switches/dt-dv-de-energized-tap-changer
| 1 Phase Pad | All | 2-position LBOR switch (1-Deck and 2-Deck) | Switch | Howard | [9 empty] | Hitachi Energy | LBOR II and III families https://www.hitachienergy.com/us/en/products-and-solutions/transformer/tap-changers/de-energized-tap-changers-and-switches/load-break-switch-type-lbor
| 1 Phase Pad | All | Fuses | Protection | See Fuse Table | [9 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 3 Phase Pad | All kva | Transformer Tank Bronze Ground Clamps |  | H-J Enterprises, Inc. |  | Kearney |  | Penn Union | [11 empty] | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | 200A Bushing Wells 12kV, 20kV, 25kV |  | Central Moloney |  | Central Moloney |  | Howard | [11 empty] | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | 200A Bushing Wells 35kV |  | Elastimold | [9 empty] | Hitachi Energy | Universal 200 amp Bushing Wells 95-150 kV BIL with fixed or removable stud see attached component product guide |  |  |  |  | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Low Voltage/Neutral Bushings |  | Cooper |  | Central Moloney |  |  |  | Howard |  | H-J Enterprises |  | Hitachi Energy | LV stud bushing family .625-1.25" diamater see attached component product guide | Elastimold |  | ERMCO |  | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Bay-o-net fuse assembly |  | RTE/Cooper | [9 empty] | Hitachi Energy | DO-III Fuse holder - See attached component product guide |  |  |  |  | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Pressure Relief Valves - Fuse Compartment |  | Qualitrol |  | Tomco |  | Heartland | [11 empty] | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Pressure Relief Valves - Secondary Compartment |  | Qualitrol |  | Viat Instruments | [13 empty] | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Pressure Relief Valves - Transformer Tank Top |  | Qualitrol | [15 empty] | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Fiber Optic Oil Level Indicator |  | Trayer |  | Heartland | [13 empty] | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Tap Changer 5-position | switch | Cooper |  | Howard | [13 empty] | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Tap Changer | switch | Cooper |  | Howard | [7 empty] | Hitachi Energy | D series https://www.hitachienergy.com/us/en/products-and-solutions/transformer/tap-changers/de-energized-tap-changers-and-switches/dt-dv-de-energized-tap-changer
| 3 Phase Pad | All kva | Non-PCB Label |  | Almetek |  | LEM | [13 empty] | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Under Oil Arrester Ground Lead Disconnet Switch |  | Cooper |  | Howard | [13 empty] | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Bay-o-net Fuse |  | Cooper |  |  |  | ERMCO | [5 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble |  |  |  | No
| 3 Phase Pad | All kva | Current Limiting Fuse |  | GE/Mersen |  | Cooper |  | Hi-Tech | [11 empty] | Completely interchangeble |  |  |  | No
|  |  | Partial Range Current Limiting |  |  |  | Eaton/Cooper |  | Hi-Tech
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC08030C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC08040C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC08050C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC08065C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC08080C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC08100C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC08125C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC08150D100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC08165D100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | Sticker | Marking | Almetek | 17261 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | Sticker | Marking | Almetek | 17262 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C04 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 3 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C06 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 3 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C08 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 3 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C10 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 3 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C12 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 3 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C14 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 3 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C16 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 3 Phase Pad |  | Bayonet Fuse | Protection | Cooper | 4000353C17 | [8 empty] | Hitachi Energy | See provided fuse table and cross reference as well as product Guide |  |  |  |  | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC23030C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC23040C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC23050C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC23080C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC23100C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | 4-Position Switch | Switch | Cooper | LS4RH3T12M | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | 2-Position LBOR Switch | Switch | Cooper/Eaton |  | Central Moloney |  | Howard | [5 empty] | Hitachi Energy | LBOR II and III families https://www.hitachienergy.com/us/en/products-and-solutions/transformer/tap-changers/de-energized-tap-changers-and-switches/load-break-switch-type-lbor
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC15030C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC15050C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC15080C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC15125C100 | [14 empty] | Completely interchangeble
| 3 Phase Pad |  | ELSP | Protection | Cooper | CBUC15150D100 | [14 empty] | Completely interchangeble
| 3 Phase Pad | All | Tank Grounding | Grounds | Penn Union | LSN-050N | [13 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| 3 Phase Pad | <500 kVA | Secodary Terminations | Connectors | HOMAC | Z3035-USL(R) Z4047-USL(R) | Can be very different depending on the utlity. Better for the utility to procure on there own. | [12 empty] | Any Zbar type set-screw | Any Zbar type set-screw | Similar build/installation | Verification of being equal |  | Yes
| 3 Phase Pad | >500 kVA | Secodary Terminations | Connectors | HOMAC | 12-Hole NEMA Spades | [13 empty] | Any 12 Hole NEMA | Any 12 Hole NEMA | Similar build/installation | Verification of being equal |  | Yes
| 3 Phase Pad | All | Primary Bushing Wells | HV Bushing | Eaton | BW150R | Eaton | 2638372C02R | Howard | [5 empty] | Hitachi Energy | Universal 200 amp Bushing Wells 95-150 kV BIL with fixed or removable stud |  |  |  | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 3 Phase Pad | All | Primary Bushing Wells | HV Bushing | Eaton | 2038214C51 |  | 9820A33H01 | Howard | [10 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 3 Phase Pad | 21kV | Bushing Inserts | Inserts | Elastimold | 2701A4 | Eaton | LBI225 | Hubbell | 9U02BAB001 | [9 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| 3 Phase Pad | 12kV | Bushing Inserts | Inserts | Elastimold | 1601A4 | Eaton | LBI215 | Hubbell | 9U02AAB001 | [9 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| 3 Phase Pad | 35kV | Bushing Inserts | Inserts
| 3 Phase Pad | All | Dielectric Fluid | Ester Fluids | Cargil | FR3 | Midel | 1215 | [11 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 3 Phase Pad | All | Fuse Cartridge | Bayonet Fuse | Eaton | 4000361C99FV | Eaton | 4000361C89FV (high current) | [11 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 3 Phase Pad | All | Fuse Cartridge | Bayonet Fuse | Eaton | [9 empty] | Hitachi Energy | See provided fuse table and cross reference
| 3 Phase Pad | All | Fuses | Protection | See Fuse Table | [9 empty] | Hitachi Energy | See provided fuse table and cross reference |  |  |  | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 3 Phase Pad |  | Dual Voltage Switches | Switch | Hitachi Energy |  | Eaton | [7 empty] | Hitachi Energy | D series https://www.hitachienergy.com/us/en/products-and-solutions/transformer/tap-changers/de-energized-tap-changers-and-switches/dt-dv-de-energized-tap-changer
| Network | All | Bushing Inserts | Inserts | Elastimold | 1601A4 | Eaton | LBI215 | Chardon | 9U02AAB001 | [9 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| Network | All | Bushing Inserts | Insulating Cap | Elastimold | 160DRG | Eaton | LPC215 | [11 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| Network | All | Dielectric Fluid | Ester Fluids | Cargil | FR3 | Midel | 1215 | [11 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| Network | All | Protector | Secondary | Eaton | CM52 | [13 empty] | None | None
| OH | All | Pressure Relief Valve | Pressure Relief | IFD | IFD-ORCA-10PSI-aA | [13 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| OH | All | Eyebolt | High Voltage Terminal | Penn Union | S46906 | [13 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| OH | All | Bird Guard | Covers | GE | 1921J060P21 | Eaton | 2600229C06 | [11 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| OH | All | Dielectric Fluid | Ester Fluids | Cargil | FR3 | Midel | 1215 | [11 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| OH 1 Phase | 50kva and smaller | Interlaced windings |  | Allowing Non-Interlaced Windings | [15 empty] | Only one manufacturer has asked for this at this time |  |  |  | No
| Network | All | Primary Bushing | HV Bushing | Central Maloney | [9 empty] | Hitachi Energy |  |  |  |  | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| OH 1 Phase | All kva | Tap Changer 5-position | switch | Howard | [6 empty] | 5 Approved Mfgs |  |  | Hitachi Energy | D series https://www.hitachienergy.com/us/en/products-and-solutions/transformer/tap-changers/de-energized-tap-changers-and-switches/dt-dv-de-energized-tap-changer | [8 empty] | No
| OH 1 Phase |  | Arrester Bracket Guard | Animal Guard | CENTRAL MOLONEY | 70380348 | Howard
| OH 1 Phase |  | Arrester Top Guard | Animal Guard | RELIAGUARD | LA-13002 | Howard
| OH 1 Phase |  | 10kV MOV | Lightning Arrester | Cooper | UHS10050AL81B1A | Maclean | ZRP010-0C00163 | HUBBELL POWER SYSTEMS | 213709-6367 | [10 empty] | Completely interchangeble
| OH 1 Phase |  | 6kV MOV | Lightning Arrester | Cooper | UHS06040A1A1B1A | Maclean | ZHP006-0C00100-0L | HUBBELL POWER SYSTEMS | 213705-7324 | GE | 9L23AXX006AC | ABB | PHO6DAD021 | [6 empty] | Completely interchangeble
| OH 1 Phase |  | 27kV MOV | Lightning Arrester | Cooper | UHS27110A1A1B1A | Maclean | ZHP027-0C00100-0L | HUBBELL POWER SYSTEMS | 213722-7324 | GE | 9L20AXX027AH | [8 empty] | Completely interchangeble
| OH 1 Phase |  | Magnex | Protection | Cooper | MX1AE1SYE12 | [14 empty] | Completely interchangeble
| OH 1 Phase |  | Magnex | Protection | Cooper | MX1AE1SYE25 | [14 empty] | Completely interchangeble
| OH 1 Phase |  | Magnex | Protection | Cooper | MX1AE1SYE30 | [14 empty] | Completely interchangeble
| OH 1 Phase |  | Magnex | Protection | Cooper | MX1AE1SYE40 | [14 empty] | Completely interchangeble
| OH 1 Phase |  | Shunt Kit F/ Magnex | Protection | Cooper | 3638535A05 | [14 empty] | Completely interchangeble
| OH 1 Phase | All kva | Dual Voltage Switches | [8 empty] | 5 Approved Mfgs |  |  | Hitachi Energy | [9 empty] | No
| OH 1 Phase |  | Isolation Link | Protection | Cooper | 36730803B10 | [8 empty] | Hitachi Energy | [5 empty] | Completely interchangeble
| OH 1 Phase |  | Isolation Link | Protection | Cooper | 36730803B03 | [8 empty] | Hitachi Energy | [5 empty] | Completely interchangeble
| OH 1 Phase |  | Isolation Link | Protection | Cooper | 36730803B05 | [8 empty] | Hitachi Energy | [5 empty] | Completely interchangeble
| Vaulted 3PH | 21kV | Bushing Inserts | Inserts | Elastimold | 2701A4 | Eaton | LBI225 | Chardon | 9U02AAB001 | [9 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| Vaulted 3PH | 12kV | Bushing Inserts | Inserts | Elastimold | 1601A4 | Eaton | LBI215 | Chardon | 9U02AAB001 | [9 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| Vaulted 3PH | 21kV | Bushing Inserts | Insulating Cap | Elastimold | 273DRG | Eaton | LPC225 | [11 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| Vaulted 3PH | 12kV | Bushing Inserts | Insulating Cap | Elastimold | 160DRG | Eaton | LPC215 | [11 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | Yes
| Vaulted 3PH | All | Primary Bushing | HV Bushing | Central Maloney | [9 empty] | Hitachi Energy |  |  |  |  | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| Vaulted 3PH | All | Dielectric Fluid | Ester Fluids | Cargil | FR3 | Midel | 1215 | [11 empty] | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 1-Phase and Three Phase pads |  | Decals required from a specfic manufacturer |  | Specified sole source decals can be difficult to obtain
| 1-Phase and Three Phase pads |  | Special Stencils |  | Require time and labor to make and apply
| Vaulted 3PH | All | Fuses | Protection | See Fuse Table | [9 empty] | Hitachi Energy |  |  |  |  | Prior Approval | Prior Approval | Similar build/installation | Verification of being equal |  | No
| 1 Phase Pad |  | Dual Voltage Switches | Switch | Hitachi Energy |  | Eaton | [7 empty] | Hitachi Energy | D series https://www.hitachienergy.com/us/en/products-and-solutions/transformer/tap-changers/de-energized-tap-changers-and-switches/dt-dv-de-energized-tap-changer
Note on N56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: We have purchased this part from these two vendors

## Fuses
Expulsion Fuses - Current Sensing
COOPER /EATON |  | ABB |  | ERMCO
Catalog Num | Current (A) | Catalog Num | Current (A) | Catalog Num | Current (A)
4000353C04 | 6 | 1B11143G04 | 6 | 9F54MFC040 | 6
4000353C06 | 10 | 1B11143G06 | 10 | 9F54MFC060 | 10
4000353C08 | 15 | 1B11143G08 | 15 | 9F54MFC080 | 15
4000353C10 | 25 | 1B11143G10 | 25 | 9F54MFC100 | 25
4000353C12 | 40 | 1B11143G12 | 40 | 9F54MFC120 | 40
4000353C14 | 65 | 1B11143G14 | 65 | 9F54MFC140 | 65
4000353C16 | 100 | 1B11143G16 | 100 | 9F54MFC160 | 100
4000353C17 | 140 | 1B11143G17 | 140 | 9F54MFC170 | 140
Expulsion Fuses - Dual Sensing
COOPER /EATON |  | ABB |  | ERMCO
Catalog Num | Current (A) | Catalog Num | Current (A) | Catalog Num | Current (A)
4000358C03 | 3 | 1B11144G03 | 3 | 9F54LFC030 | 3
4000358C05 | 8 | 1B11144G05 | 8 | 9F54LFC050 | 8
4000358C08 | 15 | 1B11144G08 | 15 | 9F54LFC080 | 15
4000358C10 | 25 | 1B11144G10 | 25 | 9F54LFC100 | 25
4000358C12 | 50 | 1B11144G12 | 50 | 9F54LFC120 | 50
4000358C14 | 65 | 1B11144G14 | 65
4000358C16 | 100
4000358C18 | 140
Expulsion Fuses - Dual Element
COOPER /EATON |  | ABB |  | ERMCO |  | KEARNEY
Catalog Num | Current (A) | Catalog Num | Current (A) | Catalog Num | Current (A) | Catalog Num | Current (A)
4038108C03 | 5 | 1B11145G03 | 5 | 9F54DFC030 | 5 | 124080-5 | 5
4038108C04 | 6 | 1B11145G04 | 6 | 9F54DFC040 | 6 | 124080-6 | 6
4038108C05 | 8 | 1B11145G05 | 8 | 9F54DFC050 | 8 | 124080-8 | 8
4038108C06 | 12 | 1B11145G06 | 12 | 9F54DFC060 | 12 | 124080-12 | 12
4038108C07 | 15 | 1B11145G07 | 15 | 9F54DFC070 | 15 | 124080-15 | 15
4038108C09 | 25 | 1B11145G09 | 25 | 9F54DFC090 | 25 | 124080-25 | 25
4038108C11 | 40 | 1B11145G11 | 40 | 9F54DFC110 | 40
4038108C12 | 50 | 1B11145G12 | 50 | 9F54DFC120 | 50
4038108C14 | 65 |  |  | 9F54DFC140 | 65
Fuses ISO Link
COOPER /EATON |  | ERMCO
Catalog Num |  | Catalog Num |  | Brand | Catalog # | Curve
3001861A01M |  | 7580ZB0299 |  | ABB | 1C11130G01 | A1
3001861A02M |  | 7580ZB0399 |  | ABB | 1C11130G02 | A2
3001861A03M |  | 7580ZB0499 |  | ABB | 1C11130G03 | A3
3001861A05M |  | 7580ZB0599 |  | ABB | 1C11130G05 | A5
3001861A06M |  | 7580ZB0699 |  | ABB | 1C11130G06 | A6
3001861A07M |  | 7580ZB0799 |  | ABB | 1C11130G07 | A7
Bayonet Fuse holder
COOPER /EATON |  | CHARDON
Catalog Num |  | Catalog Num
4000361C99FV |  | CHBONFV
Partial Range Current Limiting Fuses (CLF) (8.3 kV)
HI-TECH |  | MERSEN |  | COOPER /EATON
Catalog Num | Current (A) | Catalog Num | Current (A) | Catalog Num | Current (A) |  | Notes:
HTSS132030 | 30 | 9F59CBC030 | 30 | CBUC08030C100 | 30 |  | CLFs are not fully equivalent for the same current rating. It is required to review fuse coordination graph to confirm equivalency for a particular design application
HTSS132040 | 40 | 9F59CBC040 | 40 | CBUC08040C100 | 40 |  | Also, fuse mounting requirements are different among fuse manufacturers, and will be required to modify based on manufacturer data sheets
HTSS232040 | 40
HTSS232050 | 50 | 9F59CBC050 | 50 | CBUC08050C100 | 50
HTSS232065 | 65 | 9F59CBC065 | 65 | CBUC08065C100 | 65
HTSS232080 | 80 | 9F59CBC080 | 80 | CBUC08080C100 | 80
HTSS232100 | 100 | 9F59CBC100 | 100 | CBUC08100C100 | 100
HTSS232125 | 125 | 9F59CBC125 | 125 | CBUC08125C100 | 125
HTSS232150 | 150 | 9F59CBC150 | 150 | CBUC08150D100 | 150
HTSS232165 | 165 | 9F59CBC165 | 165 | CBUC08165D100 | 165
HTSS232200 | 200 | 9F59CBC200 | 200
Partial Range Current Limiting Fuses (CLF) (15.5-17.2 kV)
HI-TECH |  | MERSEN |  | COOPER /EATON
Catalog Num | Current (A) | Catalog Num | Current (A) | Catalog Num | Current (A) |  | Notes:
HTSS142030 | 30 | 9F59CBD030 | 30 | CBUC15030C100 | 30 |  | CLFs are not fully equivalent for the same current rating. It is required to review fuse coordination graph to confirm equivalency for a particular design application
HTSS240030 | 30 | [5 empty] | Also, fuse mounting requirements are different among fuse manufacturers, and will be required to modify based on manufacturer data sheets
HTSS142040 | 40 | 9F59CBD040 | 40 | CBUC15040C100 | 40
HTSS240040 | 40
HTSS240050 | 50 | 9F59CBD050 | 50 | CBUC15050C100 | 50
HTSS242065 | 65 | 9F59CBD065 | 65 | CBUC15065C100 | 65
HTSS242080 | 80 | 9F59CBD080 | 80 | CBUC15080C100 | 80
HTSS242100 | 100 | 9F59CBD100 | 100 | CBUC15100C100 | 100
HTSS242125 | 125 | 9F59CBD125 | 125 | CBUC15125C100 | 125
HTSS242150 | 150 | 9F59CBD150 | 150 | CBUC15150D100 | 150
HTSS242165 | 165 | 9F59CBD165 | 165 | CBUC15165D100 | 165
Partial Range Current Limiting Fuses (CLF) (23-25.5 kV)
HI-TECH |  | MERSEN |  | COOPER /EATON
Catalog Num | Current (A) | Catalog Num | Current (A) | Catalog Num | Current (A) |  | Notas:
HTSS152030 | 30 | 9F59CBE030 | 30 | CBUC23030C100 | 30 |  | Fusibles CLF no son equivalentes electricamente en todos los casos, se debera revisar la coordinacion en diseño en cuestion
HTSS252030 | 30 | [5 empty] | Antes de implementar fusible alterno, se debe revisar si se debe cambiar tambien soporte mecanico
HTSS252040 | 40 | 9F59CBE040 | 40 | CBUC23040C100 | 40
HTSS252050 | 50 | 9F59CBE050 | 50 | CBUC23050C100 | 50
HTSS252065 | 65 | 9F59CBE065 | 65 | CBUC23065C100 | 65
HTSS252080 | 80 | 9F59CBE080 | 80 | CBUC23080C100 | 80
HTSS252100 | 100 | 9F59CBE100 | 100 | CBUC23100C100 | 100
|  |  |  | CBUC23125D100 | 125
|  |  |  | CBUC23150D100 | 150
|  |  |  | CBUC23165D100 | 165
Partial Range Current Limiting Fuses (CLF) (38 kV)
HI-TECH |  | MERSEN
Catalog Num | Current (A) | Catalog Num | Current (A) |  | Notas:
HTSS372065 | 65 | 9F59CCF065 | 65 |  | Fusibles CLF no son equivalentes electricamente en todos los casos, se debera revisar la coordinacion en diseño en cuestion
HTSS372080 | 80 | 9F59CCF080 | 80 |  | Antes de implementar fusible alterno, se debe revisar si se debe cambiar tambien soporte mecanico
HTSS372100 | 100 | 9F59CCF100 | 100
HTSS372125 | 125 | 9F59CCF125 | 125
HTSS372140 | 140
HTSS372165 | 165 | 9F59CCF165 | 165
HTSS372200 | 200

## Bay-O-Net Fuses
BAY-O-NET EXPULSION FUSES
| Bay-o-Net Fuse |  |  |  | Isolation Links
Rating | Ermco | Cooper / Eaton | ABB | Kearney | Ermco | Cooper / Eaton | Chardon
(A) | Cat. Number | Cat. Number | Cat. Number | Cat. Number | Cat. Number | Cat. Number | Cat. Number
Fault Sensing / Current Sensing Fuse Links
6 | 9F54MFC040 | 4000353C04 | 1B11143G04 |  | 7580ZB0299 | 3001861A01M | CHLA01M
10 | 9F54MFC060 | 4000353C06 | 1B11143G06 |  | 7580ZB0399 | 3001861A02M | CHLA02M
15 | 9F54MFC080 | 4000353C08 | 1B11143G08 |  | 7580ZB0399 | 3001861A02M | CHLA02M
25 | 9F54MFC100 | 4000353C10 | 1B11143G10 |  | 7580ZB0499 | 3001861A03M | CHLA03M
40 | 9F54MFC120 | 4000353C12 | 1B11143G12 |  | 7580ZB0499 | 3001861A03M | CHLA03M
65 | 9F54MFC140 | 4000353C14 | 1B11143G14 |  | 7580ZB0599 | 3001861A05M | CHLA05M
100 | 9F54MFC160 | 4000353C16 | 1B11143G16 |  | 7580ZB0599 | 3001861A05M | CHLA05M
140 | 9F54MFC170 | 4000353C17 | 1B11143G17 |  | 7580ZB0599 | 3001861A05M | CHLA05M
Dual Sensing Fuse Links
3 | 9F54LFC030 | 4000358C03 | 1B11144G03 |  | 7580ZB0299 | 3001861A01M | CHLA01M
8 | 9F54LFC050 | 4000358C05 | 1B11144G05 |  | 7580ZB0399 | 3001861A02M | CHLA02M
15 | 9F54LFC080 | 4000358C08 | 1B11144G08 |  | 7580ZB0499 | 3001861A03M | CHLA03M
25 | 9F54LFC100 | 4000358C10 | 1B11144G10 |  | 7580ZB0599 | 3001861A05M | CHLA05M
50 | 9F54LFC120 | 4000358C12 | 1B11144G12 |  | 7580ZB0699 | 3001861A06M | CHLA06M
65 |  | 4000358C14 | 1B11144G14 |  | 7580ZB0799 | 3001861A07M | CHLA07M
100 |  | 4000358C16CB* |  |  | 7580ZB0799 | 3001861A07M | CHLA07M
140 |  | 4000358C18CB* |  |  | 7580ZB0799 | 3001861A07M | CHLA07M
*Do not use fuse links 358C16CB or C18CB for voltages greater than 8320 V for delta configurations or 14400GrdY/8320.
Dual Element Fuse Links
5 | 9F54DFC030 | 4038108C03 | 1B11145G03 | 124080-5 | 7580ZB0299 | 3001861A01M | CHLA01M
6 | 9F54DFC040 | 4038108C04 | 1B11145G04 | 124080-6 | 7580ZB0299 | 3001861A01M | CHLA01M
8 | 9F54DFC050 | 4038108C05 | 1B11145G05 | 124080-8 | 7580ZB0399 | 3001861A02M | CHLA02M
12 | 9F54DFC060 | 4038108C06 | 1B11145G06 | 124080-12 | 7580ZB0399 | 3001861A02M | CHLA02M
15 | 9F54DFC070 | 4038108C07 | 1B11145G07 | 124080-15 | 7580ZB0399 | 3001861A02M | CHLA02M
25 | 9F54DFC090 | 4038108C09 | 1B11145G09 | 124080-25 | 7580ZB0499 | 3001861A03M | CHLA03M
40 | 9F54DFC110 | 4038108C11 | 1B11145G11 | 124080-30 | 7580ZB0499 | 3001861A03M | CHLA03M
50 | 9F54DFC120 | 4038108C12 | 1B11145G12 | 124080-35 | 7580ZB0499 | 3001861A03M | CHLA03M
65 | 9F54DFC140 | 4038108C14 |  |  | 7580ZB0599 | 3001861A05M | CHLA05M
High Ampere Overload Fuse Links
135 |  | 4038361C03CB |  |  | 7580ZB0599 | 3001861A05M | CHLA05M
165 |  | 4038361C04CB |  |  | 7580ZB0599 | 3001861A05M | CHLA05M
185 |  | 4038361C05CB |  |  | 7580ZB0699 | 3001861A06M | CHLA06M
200 |  | 4038361C10CB*
*Shorting Bar (Solid Link)

## High Current Epoxy LV Bushings
Family | Description | CELECO | H-J Enterprises, Inc. | Matrix | CROSSLINK | ABB | Chardon | GE | Ohio Brass | Comentarios
High Current Epoxy LV Bushings | LV BUSH 2.5kV BIL 45 2200A 4H | 1-1-9-01 B1876 | EPC10-510-000-0AE01T. |  | 85-410C04ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 2200A 6H | 1-1-9-01 B1877 | EPC 10-510-001OAE01T |  | 85-410C06ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 2200A 8H | 1-1-9-01 B1878 | EPC 10-510-002-0AE01T. |  | 85-410C08ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 2200A 10H | 1-1-9-01 B1879 | EPC10-510-002-0AE01T. |  | 85-410C10ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 2200A 12H | 1-1-9-01 B1880 | EPC10-510-004-0AE01T. |  | 85-410C12ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 2200A 14H | [8 empty] | Aún no desarrollado por Prolec/Si se requiere se puede dar de alta y solicitar inventario
| LV BUSH 2.5kV BIL 45 2200A 16H | 1-1-9-01 B1882 | EPC 10-510-0060AE01T. |  | 85-410C16ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 2200A 18H | [8 empty] | Aún no desarrollado por Prolec/Si se requiere se puede dar de alta y solicitar inventario
| LV BUSH 2.5kV BIL 45 2200A 20H | 1-1-9-01 B1884 | EPC 10-510-0080AE01T. |  | 85-410C20ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 3300A 4H | 1-1-9-02 B1885 | EPC 10-510-100-0AE01T. |  | 85-411C04ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 3300A 6H | [8 empty] | Aún no desarrollado por Prolec/Si se requiere se puede dar de alta y solicitar inventario
| LV BUSH 2.5kV BIL 45 3300A 8H | 1-1-9-02 B1887 | EPC 10-510-102-0AE01T. |  | 85-411C08ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 3300A 10H | 1-1-9-02 B1888 | EPC 10-510-103OAE01T |  | 85-411C10ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 3300A 12H | 1-1-9-02 B1889 | EPC 10-510-104-0AE01T. |  | 85-411C12ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 3300A 14H | [8 empty] | Aún no desarrollado por Prolec/Si se requiere se puede dar de alta y solicitar inventario
| LV BUSH 2.5kV BIL 45 3300A 16H | 1-1-9-02 B1891 | EPC 10-510-106OAE01T |  | 85-411C16ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 3300A 18H | [8 empty] | Aún no desarrollado por Prolec/Si se requiere se puede dar de alta y solicitar inventario
| LV BUSH 2.5kV BIL 45 3300A 20H | 1-1-9-02 B1893 | EPC 10-510-108OAE01T |  | 85-411C20ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 4515A 4H | 1-1-9-03 B1894 | EPC 10-510-200-0AE01T. |  | 85-412C04ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 4515A 6H |  |  |  | 1.2 KV, ESP 4 BARR, COBRE, 2200 A |  |  |  |  | Aún no desarrollado por Prolec/Si se requiere se puede dar de alta y solicitar inventario
| LV BUSH 2.5kV BIL 45 4515A 8H | 1-1-9-03 B1896 | EPC 10-510-202-0AE01T. |  | 85-412C08ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 4515A 10H | 1-1-9-03 B1897 | EPC 10-510-203OAE01T. |  | 85-412C10ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 4515A 12H | 1-1-9-03 B1898 | EPC 10-510-204-0AE01T. |  | 85-412C12ID |  |  |  |  | Aún no desarrollado por Prolec/Si se requiere se puede dar de alta y solicitar inventario
| LV BUSH 2.5kV BIL 45 4515A 14H | [8 empty] | Aún no desarrollado por Prolec/Si se requiere se puede dar de alta y solicitar inventario
| LV BUSH 2.5kV BIL 45 4515A 16H | 1-1-9-03 B1900 | EPC 10-510-206OAE01T |  | 85-412C16ID |  |  |  |  | Material disponible en Celeco y en tránsito
| LV BUSH 2.5kV BIL 45 4515A 18H | [8 empty] | Aún no desarrollado por Prolec/Si se requiere se puede dar de alta y solicitar inventario
| LV BUSH 2.5kV BIL 45 4515A 20H | 1-1-9-03 B1902 | EPC 10-510-208OAE01T |  | 85-412C20ID |  |  |  |  | Material disponible en Celeco y en tránsito

## HV Bushings
Bushing Well Removable Stud (35 kV, 200 Amps)
CENTRAL MOLONEY | COOPER /EATON | CELECO | ELASTIMOLD
Catalog Num | Catalog Num | Catalog Num | Catalog Num
70191972 | BW150R | B1965 | L1601-PC-S1R
L1601-PC-S2R
Bushing Well Fixed Stud (35 kV, 200 Amps)
CENTRAL MOLONEY | COOPER /EATON | CELECO | ELASTIMOLD
Catalog Num | Catalog Num | Catalog Num | Catalog Num
70191952 | BW150F | B1963 | K1601PC-S2
Integral Deadbreak Bushing (25 kV, 600 Amps)
COOPER /EATON | ELASTIMOLD | *Note:
Catalog Num | Catalog Num | Bushings are not mechanically fully interchageable
DB625B125 | K650T1 | Hole dimensions and mounting studs location changes
Integral Loadbreak Bushing (35 kV, 200 Amps)
COOPER /EATON | ERMCO
Catalog Num | Catalog Num
LB235B150GC | 9U02DBC002
Integral Deadbreak Bushing (35 kV, 600 Amps)
COOPER /EATON | CELECO
Catalog Num | Catalog Num
DB635B150 | EOB361K

## LV Bushings
Epoxy LV Bushing (1 inch stud, 1500 A)
CELECO | CENTRAL MOLONEY
Catalog Num | Catalog Num
B1743 | CM70133452-S
Epoxy LV Bushing (2200 A)
CELECO | ABB
Catalog Num | Catalog Num
B1984 | 2104C16G03

## Bushing Inserts
Single Inserts (15 kV, 200 A)
COOPER / EATON | CELECO | HUBBELL | ELASTIMOLD
Catalog Num | Catalog Num | Catalog Num | Catalog Num
LBI215BP | LBI120 | 215BIHJ | 1601A4
Double Inserts (15 kV, 200 A)
COOPER / EATON | ELASTIMOLD
Catalog Num | Catalog Num
LFI215K | 1602A3R
Single Inserts (25 kV, 200 A)
COOPER / EATON | CELECO | HUBBELL | ELASTIMOLD
Catalog Num | Catalog Num | Catalog Num | Catalog Num
LBI225BP | LBI220 | 225BIHJ | 2701A4

## Arresters
MOV Arrester (15 kV Class, Rating 10 kV, MCOV 8.4 kV)
COOPER / EATON | HUBBELL
Catalog Num | Catalog Num
3238018C10M | 215ELA10
MOV Arrester (15 kV Class, Rating 12 kV, MCOV 10.2 kV)
COOPER / EATON | HUBBELL
Catalog Num | Catalog Num
3238018C12M | 215ELA12
MOV Arrester (15 kV Class, Rating 15 kV, MCOV 12.7 kV)
COOPER / EATON | HUBBELL
Catalog Num | Catalog Num
3238018C15M | 215ELA15
MOV Arrester (15 kV Class, Rating 18 kV, MCOV 15.3 kV)
COOPER / EATON | HUBBELL
Catalog Num | Catalog Num
3238018C18M | 215ELA18
MOV Arrester (25 kV Class, Rating 18 kV, MCOV 15.3 kV)
COOPER / EATON | HUBBELL
Catalog Num | Catalog Num
3238019C18M | 225ELA18
MOV Arrester (35 kV Class, Rating 27 kV, MCOV 22 kV)
COOPER / EATON | HUBBELL
Catalog Num | Catalog Num
3238020C27M | 235ELA27

## Others
2 Position Loadbreak Switch (38 kV, 300 A)
CENTRAL MOLONEY | COOPER / EATON
Catalog Num | Catalog Num
CM70343660 | LS2R338H3N1A
LS2R338H3N1AP
Pressure Relief Valve (35 SCFM, 10 psi)
VIAT | QUALITROL
Catalog Num | Catalog Num
301-010-01N | 201-020-01

## BayoExpCross
Hitachi Energy (Formerly ABB) to Eaton (Fomerly Cooper) bayonet fuse Cross Reference
Manufacturer | Catalog Number | DESCRIPTION | TYPE | Sub type | Amps | Manufacturer | Catalog Number | DESCRIPTION | TYPE | Sub type | Amps
HITACHI(ALAMO) | 1B11143G04 | ALAMO 6AMP CUR SEN FUSE 1B11143G04 | BAYONET FUSE | Current Sensing | 6 | Eaton | 4000353C04 | EATON FAULT SENSING LINK #353C04 6 AMP | BAYONET FUSE | Current Sensing | 6
HITACHI(ALAMO) | 1B11143G06 | ALAMO 10AMP CUR SEN FUSE 1B11143G06 | BAYONET FUSE | Current Sensing | 10 | Eaton | 4000353C06 | EATON FAULT SENSING LINK #353C06 10 AM | BAYONET FUSE | Current Sensing | 10
HITACHI(ALAMO) | 1B11143G08 | ALAMO 15AMP CUR SEN FUSE 1B11143G08 | BAYONET FUSE | Current Sensing | 15 | Eaton | 4000353C08 | EATON FAULT SENSING LINK #353C08 15 AM | BAYONET FUSE | Current Sensing | 15
HITACHI(ALAMO) | 1B11143G10 | ALAMO 25AMP CUR SEN FUSE 1B11143G10 | BAYONET FUSE | Current Sensing | 25 | Eaton | 4000353C10 | EATON FAULT SENSING LINK #353C10 25 AM | BAYONET FUSE | Current Sensing | 25
HITACHI(ALAMO) | 1B11143G12 | ALAMO 40AMP CUR SEN FUSE 1B11143G12 | BAYONET FUSE | Current Sensing | 40 | Eaton | 4000353C12 | EATON FAULT SENSING LINK #353C12 40 AM | BAYONET FUSE | Current Sensing | 40
HITACHI(ALAMO) | 1B11143G14 | ALAMO 65AMP CUR SEN FUSE 1B11143G14 | BAYONET FUSE | Current Sensing | 65 | Eaton | 4000353C14 | EATON FAULT SENSING LINK #353C14 65 AM | BAYONET FUSE | Current Sensing | 65
HITACHI(ALAMO) | 1B11143G16 | ALAMO 100AMP CUR SEN FUSE 1B11143G16 | BAYONET FUSE | Current Sensing | 100 | Eaton | 4000353C16 | EATON FAULT SENSING LINK #353C16 100 A | BAYONET FUSE | Current Sensing | 100
HITACHI(ALAMO) | 1B11143G17 | ALAMO 140AMP CUR SEN FUSE 1B11143G17 | BAYONET FUSE | Current Sensing | 140 | Eaton | 4000353C17 | EATON FAULT SENSING LINK #353C17 140 A | BAYONET FUSE | Current Sensing | 140
HITACHI(ALAMO) | 1B11144G03 | ALAMO 3AMP DUAL SEN FUSE 1B11144G03 | BAYONET FUSE | Dual Sensing | 3 | Eaton | 4000358C03 | EATON OVERLOAD SENSING LINK #358C03 3 | BAYONET FUSE | Dual Sensing | 3
HITACHI(ALAMO) | 1B11144G05 | ALAMO 8AMP DUAL SEN FUSE 1B11144G05 | BAYONET FUSE | Dual Sensing | 8 | Eaton | 4000358C05 | EATON OVERLOAD SENSING LINK #358C05 8 | BAYONET FUSE | Dual Sensing | 8
HITACHI(ALAMO) | 1B11144G08 | ALAMO 15AMP DUAL SEN FUSE 1B11144G08 | BAYONET FUSE | Dual Sensing | 15 | Eaton | 4000358C08 | EATON OVERLOAD SENSING LINK #358C08 15 | BAYONET FUSE | Dual Sensing | 15
HITACHI(ALAMO) | 1B11144G10 | ALAMO 25AMP DUAL SEN FUSE 1B11144G10 | BAYONET FUSE | Dual Sensing | 25 | Eaton | 4000358C10 | EATON OVERLOAD SENSING LINK #358C10 25 | BAYONET FUSE | Dual Sensing | 25
HITACHI(ALAMO) | 1B11144G12 | ALAMO 50AMP DUAL SEN FUSE 1B11144G12 | BAYONET FUSE | Dual Sensing | 50 | Eaton | 4000358C12 | EATON OVERLOAD SENSING LINK #358C12 50 | BAYONET FUSE | Dual Sensing | 50
HITACHI(ALAMO) | 1B11144G14 | ALAMO 65AMP DUAL SEN FUSE 1B11144G14 | BAYONET FUSE | Dual Sensing | 65 | Eaton | 4000358C14 | EATON OVERLOAD SENSING LINK #358C14 65 | BAYONET FUSE | Dual Sensing | 65
[6 empty] | Eaton | 4000358C16C | EATON OVERLOAD SENSING LINK #358C16 100 | BAYONET FUSE | Dual Sensing | 100
[6 empty] | Eaton | 4000358C18C | EATON OVERLOAD SENSING LINK #358C18 140 | BAYONET FUSE | Dual Sensing | 140
HITACHI(ALAMO) | 1B11145G03 | ALAMO 5AMP DUAL ELE FUSE 1B11145G03 | BAYONET FUSE | Dual Element | 5 | Eaton | 4038108C03 | EATON DUAL ELEMENT 4038108C03 5 AMP | BAYONET FUSE | Dual Element | 5
HITACHI(ALAMO) | 1B11145G04 | ALAMO 6AMP DUAL ELE FUSE 1B11145G04 | BAYONET FUSE | Dual Element | 6 | Eaton | 4038108C04 | EATON DUAL ELEMENT 4038108C04 6 AMP | BAYONET FUSE | Dual Element | 6
HITACHI(ALAMO) | 1B11145G05 | ALAMO 8AMP DUAL ELE FUSE 1B11145G05 | BAYONET FUSE | Dual Element | 8 | Eaton | 4038108C05 | EATON DUAL ELEMENT 4038108C05 8 AMP | BAYONET FUSE | Dual Element | 8
HITACHI(ALAMO) | 1B11145G06 | ALAMO 12AMP DUAL ELE FUSE 1B11145G06 | BAYONET FUSE | Dual Element | 12 | Eaton | 4038108C06 | EATON DUAL ELEMENT 4038108C06 12 AMP | BAYONET FUSE | Dual Element | 12
HITACHI(ALAMO) | 1B11145G07 | ALAMO 15AMP DUAL ELE FUSE 1B11145G07 | BAYONET FUSE | Dual Element | 15 | Eaton | 4038108C07 | EATON DUAL ELEMENT 4038108C07 15 AMP | BAYONET FUSE | Dual Element | 15
HITACHI(ALAMO) | 1B11145G09 | ALAMO 25AMP DUAL ELE FUSE 1B11145G09 | BAYONET FUSE | Dual Element | 25 | Eaton | 4038108C09 | EATON DUAL ELEMENT 4038108C09 25 AMP | BAYONET FUSE | Dual Element | 25
HITACHI(ALAMO) | 1B11145G11 | ALAMO 40AMP DUAL ELE FUSE 1B11145G11 | BAYONET FUSE | Dual Element | 40 | Eaton | 4038108C11 | EATON DUAL ELEMENT 4038108C11 40 AMP | BAYONET FUSE | Dual Element | 40
HITACHI(ALAMO) | 1B11145G12 | ALAMO 50AMP DUAL ELE FUSE 1B11145G12 | BAYONET FUSE | Dual Element | 50 | Eaton | 4038108C12 | EATON DUAL ELEMENT 4038108C12 50 AMP | BAYONET FUSE | Dual Element | 50
[6 empty] | Eaton | 4038108C14 | EATON DUAL ELEMENT 4038108C14 65 AMP | BAYONET FUSE | Dual Element | 65

## 1PH PM Fusing
Transformer Primary Voltage | Xfmr | Fuse Rated Voltage | Fuse Type | RTE/ | Fuse Type | Cooper ELSP
kV | kVA | kV | RTE/Cooper | Cooper | Cooper ELSP or ELX Current Limiting | Current Limiting (Oil Immersed) Fuse Size
|  |  | Bay-O-Net | Bay-O-Net
|  |  | Dual Sensing, or High Ampere | Fuse Size
12GY/6.9 | 15 | 15.5 | 4000358C03 | 3 | 3544030M61M | 30
12GY/6.9 | 25 | 15.5 | 4000358C05 | 8 | 3545030M61M | 30
12GY/6.9 | 50 | 15.5 | 4000358C08 | 15 | CBUC08050C100 | 50
12GY/6.9 | 75 | 15.5 | 4000358C08 | 15 | CBUC08080C100 | 80
12GY/6.9 | 100 | 15.5 | 4000358C10 | 25 | CBUC08100C100 | 100
12GY/6.9 | 167 | 15.5 | 4000358C12 | 50 | CBUC08125C100 | 125
21GY/12 | 50 | 15.5 | 4000358C05 | 8 | 3545030M61M | 30
21GY/12 | 75 | 15.5 | 4000358C08 | 15 | CBUC23030C100 | 30
21GY/12 | 100 | 15.5 | 4000358C08 | 15 | CBUC23040C100 | 40
21GY/12 | 167 | 15.5 | 4000358C10 | 25 | CBUC23080C100 | 80
12 | 15 | 15.5 | 4000358C03 | 3 | 3544030M61M | 30
12 | 25 | 15.5 | 4000358C03 | 3 | 3544030M61M | 30
12 | 50 | 15.5 | 4000358C05 | 8 | CBUC15030C100 | 30
12 | 75 | 15.5 | 4000358C08 | 15 | CBUC15050C100 | 50
12 | 100 | 15.5 | 4000358C08 | 15 | CBUC15050C100 | 50
12 | 167 | 15.5 | 4000358C10 | 25 | CBUC15100C100 | 100
4x12* | 50 | 15.5 | 4000358C10 | 25 | CBUC15030C100 | 30
4x12* | 100 | 15.5 | 4000358C12 | 50 | CBUC15050C100 | 50

## 3PH PM Fusing
System | Xfmr | Xfmr Primary Connection | Fuse Type | Cooper | Fuse Type | Cooper ELSP
kV | kVA |  | Cooper | Bay-O-Net | Cooper | Current Limiting (Oil Immersed) Fuse Size
|  |  | Bay-O-Net | Fuse Rating | ELSP
|  |  | Dual Sensing or High Ampere |  | Current Limiting
12 | 45 | Delta or Wye | 4000358C03 | 3 | 3544030M61M | 30
12 | 75 | Delta or Wye | 4000358C05 | 8 | CBUC15030C100 | 30
12 | 112.5 | Delta or Wye | 4000358C08 | 15 | CBUC15050C100 | 50
12 | 150 | Delta or Wye | 4000358C08 | 15 | CBUC15065C100 | 65
12 | 225 | Delta or Wye | 4000358C10 | 25 | CBUC15100C100 | 100
12 | 300 | Delta or Wye | 4000358C10 | 25 | CBUC15100C100 | 100
12 | 500 | Delta or Wye | 4000358C12 | 50 | CBUC15150D100 | 150
12 | 750 | Delta or Wye | 4000358C14 | 65 | CBUC15165D100 | 165
12 | 1000 | Delta or Wye | 4000358C14 | 65 | CBUC15125C1002 | 250 (2-125s) 2
12 | 1500 | Delta or Wye | 4038361C05CB | 125 | CBUC15125C1002 | 250 (2-125s) 2
12 | 2000 | Delta or Wye | 4038361C05CB | 125 | CBUC15125C1002 | 250 (2-125s) 2
12 | 2500 | Delta or Wye | 4038361C05CB | 125 | CBUC15150D1002 | 300 (2-150s) 2
21 | 45 | Delta or Wye | 4000358C03 | 3 | 3545030M61M | 30
21 | 75 | Delta or Wye | 4000358C03 | 3 | 3545030M61M | 30
21 | 112.5 | Delta or Wye | 4000358C05 | 8 | CBUC23030C100 | 30
21 | 150 | Delta or Wye | 4000358C05 | 8 | CBUC23030C100 | 30
21 | 225 | Delta or Wye | 4000358C08 | 15 | CBUC23050C100 | 50
21 | 300 | Delta or Wye | 4000358C08 | 15 | CBUC23050C100 | 50
21 | 500 | Delta or Wye | 4000358C10 | 25 | CBUC23080C100 | 80
21 | 750 | Delta or Wye | 4000358C12 | 50 | CBUC23125D100 | 125
21 | 1000 | Delta or Wye | 4000358C12 | 50 | CBUC23125D100 | 125
21 | 1500 | Wye only | 4038361C03CB 3 | 65 | CBUC23150D100 | 150
21 | 2000 | Wye only | 4038361C04CB 3 | 100 | CBUC23165D100 | 165
21 | 2500 | Wye only | 4038361C05CB 3 | 125 | CBUC23125D100 2 | 250 (2-125s) 2
21 | 1500 | Delta only | 4000353C14 1 | 65 | CBUC23150D1001 | 1501
21 | 2000 | Delta only | 4000358C14 1 | 65 | CBUC23125D100 2 | 250 (2-125s) 2
21 | 2500 | Delta only | 4000353C16 1 | 100 | CBUC23125D100 2 | 250 (2-125s) 2

## Vaulted Fusing
System | Xfmr | Xfmr | Fuse Type | Cooper | Fuse Type | Cooper
kV | kVA | Primary | Cooper | Bay-O-Net | Cooper | Current Limiting (Oil Immersed) Fuse Size
|  | Connection | Bay-O-Net | Fuse Rating | ELSP 15 or ELX 37
|  |  | Dual Sensing, or, High Ampere |  | Current Limiting
12 | 45 | Delta or Wye | 4000358C03 | 3 | 3544030M61M | 30
12 | 75 | Delta or Wye | 4000358C05 | 8 | CBUC15030C100 | 30
12 | 112.5 | Delta or Wye | 4000358C08 | 15 | CBUC15050C100 | 50
12 | 150 | Delta or Wye | 4000358C08 | 15 | CBUC15065C100 | 65
12 | 225 | Delta or Wye | 4000358C010 | 25 | CBUC15100C100 | 100
12 | 300 | Delta or Wye | 4000358C10 | 25 | CBUC15100C100 | 100
12 | 500 | Delta or Wye | 4000358C12 | 50 | CBUC15150D100 | 150
12 | 750 | Delta or Wye | 4000358C14 | 65 | CBUC15165D100 | 165
12 | 1000 | Delta or Wye | 4000358C14 | 65 | CBUC15125C100 2 | 250 (2-125s) 2
12 | 1500 | Delta or Wye | 4038361C05CB | 125 | CBUC15125C100 2 | 250 (2-125s) 2
12 | 2000 | Delta or Wye | 4038361C05CB | 125 | CBUC15125C100 2 | 250 (2-125s) 2
12 | 2500 | Delta or Wye | 4038361C05CB | 125 | CBUC15150D100 2 | 300 (2-150s) 2
20.8 | 45 | Delta or Wye | 4000358C03 | 3 | 3545030M61M | 30
20.8 | 75 | Delta or Wye | 4000358C03 | 3 | 3545030M61M | 30
20.8 | 112.5 | Delta or Wye | 4000358C05 | 8 | CBUC23030C100 | 30
20.8 | 150 | Delta or Wye | 4000358C05 | 8 | CBUC23030C100 | 30
20.8 | 225 | Delta or Wye | 4000358C08 | 15 | CBUC23050C100 | 50
20.8 | 300 | Delta or Wye | 4000358C08 | 15 | CBUC23050C100 | 50
20.8 | 500 | Delta or Wye | 4000358C10 | 25 | CBUC23080C100 | 80
20.8 | 750 | Delta or Wye | 4000358C12 | 50 | CBUC23125DC100 | 125
20.8 | 1000 | Delta or Wye | 4000358C12 | 50 | CBUC23125DC100 | 125
20.8 | 1500 | Delta or Wye | None | None | 3565025M11M 2, 3 | 50 (2-25s) 2, 3
20.8 | 2000 | Delta or Wye | None | None | 3565030M11M 2, 3 | 60 (2-30s) 2, 3
20.8 | 2500 | Delta or Wye | None | None | 3565040M11M 2, 3 | 80 (2-40s) 2, 3