## Config List_1P OH
Minimalist Configuration | Standard Baseline Configuration | Custom Utility Specific Configuration
1 Phase Overhead
Mild Steel Tank with IEEE C57.12.28 Coating System
ANSI #24 (dark gray) or ANSI #70 (light gray) paint. Coating system to meet IEEE
Stainless Steel Tank and/or covers (Grades 304 or 409)
No Switches on LV or HV
Dual Voltage switch standard 2:1 ratio
Optional Taps in HV winding, 2 above and 2 below, of 2.5%
4 Position Switches
No fusing or Secondary breaker protection
Current Limiting Fuse
CSP units with LV Breaker
HV breaker (Magnex)
Secondary circuit breaker protection with indictor light (CSP transformer)
Expulsion fuse in HV
Under Oil Arresters
Lightning arresters & mounting bracket
Lightning Mitigation Design Considerations
Custom fuses in terminal board in HV
Single Cooling rating 65°C AWR
Special AWR ratings (55°C)
Special AWR (75°C), with high temperature insulating liquids (natural ester)
Fluid - mineral oil
Dielectric Fluids -- Mineral Oil or Esters
Standard Impedance as per DOE
Minimum Impedance as per IEEE Stds.
Required Impedance Ranges
Single Hanger Mounting
Single or Double Hanger Mounting
Two sets of support lugs (RUS spec.)
Primary Bushing Rated for System Voltage
1 or 2 bushings in HV, 3 or 4 bushings in LV, livefront type
Secondary terminations
Primary Bushing Creep Distance
Standard pressure-relief system (PRV)
Cover grounding connection
Tank grounding connector (accepts #8 to #2 AWG conductor)
Internal Fault Detector
Vacuum Pressure Gauge
15kV Insulated covers
Wildlife protection
Special BIL requirements in HV
Nameplate
Standard Nameplate on support lug
Labeling / Branding Requirements
Custom markings (decals or stencils: Non PCB, warning, Customer ID numbers, Barcode Labels)

## Config List_1P Pad
Minimalist Configuration | Standard Baseline Configuration | Custom Utility Specific Configuration
1 Phase Pad Mount | 1 Phase Pad Mount | 1 Phase Pad Mount
Mild Steel Tank with IEEE C57.12.28 Coating System
Tank and compartment with doors to prevent access to terminals and connections
Compliance with IEEE C57.12.28 Enclosure Integrity (Mechanical (Tamper proof), and Coating System Performance)
Full Stainless Steel Tank and compartment enclosure (Grades 304 or 409)
300 stainless steel sill
Special spacing and locations of components on front tank wall
Special colors (Gray ANSI 70, Desert Tan)
Deeper Cabinet
Footprint Requirements
No Switches on LV or HV
No taps in HV winding
Radial or Loop feed terminal arrangement
Dual Voltage switch standard 2:1 or 3:1 ratios
Tap changer ((2) +/- 2.5% taps)
Tap Changers (5 position, 7 Position)
DeEnergized Tap Changer
Loadbreak ON/OFF switch
Sectionalizing loadbreak switches
4160x12kV Primary
Bayonet Fusing with Isolation Link
Protection (Bay-o-nets/ELSP)
Protection -- Magnex Breakers
LV in Line Terminals mounted on LV bushing studs
Lightning arrester attachment
Secondary Arrester -- Internal/External MOV
Secondary connectors (zbars, covered/not covered)
HV fusing with general purpose partial range current limiting fuse, internally mounted
19.9kV Under Oil Arresters
Special fusing with full range current limiting fuse with cannister fuse holder
Custom fuses in terminal board in HV
Primary bushing arrangement - standard per IEEE - TYPE 2 A
Seconary bushing arrangement - standard per IEEE - TYPE 2 A
Primary bushing arrangement - standard per IEEE - TYPE 2 or TYPE 1
Seconary bushing arrangement - standard per IEEE - TYPE 2 or TYPE 1
Specific Bushing Layout
Loop fed (2 primary bushings)
Preapproved bushing inserts.
Single Cooling rating 65°C AWR
Fluid - mineral oil
Fluid (Ester)
Special AWR ratings (55°C)
Special AWR (75°C), with high temperature insulating liquids (natural ester)
Minimum BIL ratings
Standard Impedance as per DOE
Compliance with BIL and Dielectric Test Requirements
Minimum Impedance as per IEEE Stds.
Special BIL requirements in HV
Pressure relief valve
Nameplate
Oil fill provision - standard per IEEE
Oil drain provision - standard per IEEE
Lifting provisions
LV ground connector and/or connection
Parking stands in HV compartment
Ground connector in tank
Internal Fault Detector
provisions for a 9/16" dia padlock. Hex bolts for securing bolts
Clearance and Warning stickers per Company design
Copper Oxide on door latch hardware
Vacuum Pressure Gauge
Ground Clamps
Drain valve with sampling
Plastic Drip shield for Bayonet
Custom markings (decals or stencils: Non PCB, warning, Customer ID numbers, Barcode Labels)
Thermometer
Liquid Level Gauge

## Config List_3P Pad
Minimalist Configuration | Standard Baseline Configuration | Custom Utility Specific Configuration
3 Phase Pad Mount | 3 Phase Pad Mount | 3 Phase Pad Mount
Mild Steel Tank with IEEE C57.12.28 Coating System
Sealed tank construction with welded cover and bolted handhole
Tank and compartment with doors to prevent access to terminals and connections
Compliance with IEEE C57.12.28 Enclosure Integrity (Mechanical (Tamper proof), and Coating System Performance)
Coating system to meet IEEE, Green color
Terminal arrangement as per compartment configuration of IEEE Stds.
Full Stainless Steel Tank and compartment enclosure (Grades 304 or 409)
Special spacing and locations of components on front tank wall
HV compartment on the left, LV compartment on the right. HV compartment can't be opened without opening the LV compartment
HV and LV compartments seperated by a barrier of metal or other rigid material
Special spacing and locations of components on front tank wall
Partial Stainless Steel Tank and compartment enclosure (Grades 304 or 409)
Special colors (Gray ANSI 70, Desert Tan)
Custom Mechanical structures (Ducts, flanges, Throaths) for HV or LV connections
Primary feed - radial
Single voltage primary (no Dual Voltage)
No taps
No Switches on LV or HV
Full Capacity Windings HV and LV
Standard neutral configuration per IEEE
Radial or Loop feed arrangement in HV
DE-energized tap changer with external operation
Dual Voltage switch standard 2:1 or 3:1 ratios
Tap changer ((2) +/- 2.5% taps)
Netural options
ON/OFF loadbreak switches
Sectionalizing loadbreak switches
5 legged design or 3 separate core assemblies
Eaton 4 position switch on primary side to de-energize transformer without "bliping" downstream customers.
4160x12kV Primary
Tap Changers (5 position, 7 Position)
K Factor (Design for Loads with high harmonic content)
No fusing or Secondary breaker protection
Bayonet fusing and isolation link
HV fusing with general purpose partial range current limiting fuse, internally mounted
Internal fusing
VFI for 2000kVA and up
Coil switch (on/off)
4 Position Switches
Special fusing with full range current limiting fuse with cannister fuse holder
Arresters
Under Oil Arresters
Secondary Arrester -- Internal/External MOV
Secondary termination - Live front spade connectors
Seconary bushing arrangement - standard per IEEE
Primary termination - 35 kV, 200 amp bushing wells
No inserts
Deadfront bushings in HV
Livefront bushings in LV
Primary termination - 35 kV, 200 amp bushing wells
No inserts
Primary bushing arrangement - standard per IEEE (specific dimensions)
Secondary termination - Live front spade connectors
Seconary bushing arrangement - standard per IEEE (specific dimensions)
Specific Bushing Layout
Custom spade terminals mounted on LV bushings and mechanically supported
12-hole NEMA pads for secondary connectors
Supplied with Primary bushings.
Preapproved bushing inserts.
Special LV terminals with number of holes above IEEE Stds., and customized mechanical support structures
Standard Impedance as per DOE
Minimum BIL
Single Cooling rating 65°C AWR
95kV BIL for 15kV, 150kV BIL for 35kV units
Impedance requirements
Special AWR ratings (55°C)
Special AWR (75°C), with high temperature insulating liquids (natural ester)
Fluid - mineral oil
Fluid Mineral Oil or Ester
Nameplate
Standard Danger and Warning Safety Labels - NEMA 260
Manufacturered after 1979 sticker
Clearance and Warning stickers per Company design
Custom markings (decals or stencils: Non PCB, warning, Customer ID numbers, Barcode Labels)
Branding requirements
Oil fill provision - standard per IEEE
Oil drain provision - standard per IEEE
No gauges
Ground connector in tank
Jacking facilities for lifting
Parking stands in HV compartment
Standard pressure-relief system (PRV)
Copper Oxide on door latch hardware
Vacuum Pressure Gauge
Drain valve with sampling
Temperature Gauge
Internal Fault Detector
Liquid Level Gauge
provisions for a 9/16" dia padlock. Hex bolts for securing bolts
Solid Insulation
Plastic Drip shield for Bayonet