## Guidelines
Spreadsheet | What was collected | How to view it | What you can do
Taxonomy | Input on critical design attributes and options associated with requirements and specification. Relevant standards were not included, but can be if the team feels it would be beneficial. | Three column listing: Attribute Description/Material or measurement Comments or clarifications | Please add any additional items/comments/clarification to the table that would be important for communication between multiple manufacturers, regions, and utility groups.
Attributes | There were 4 key areas of input: kVA Rating: Groupings for 1Ph Pole, 3Ph Pole, 1Ph Pad, 3Ph Pad, Network Protection: Conventional, CSP, Fused Bushing Class for 1 Ph Pole Top BIL Rating -- the base BIL rating specified for each voltage grouping | Items not in the initial tables are marked in orange. From utilities, the request was to color code the responses as: Red -- critical to keep Yellow -- not functionally necessary but requires acceptance Green -- units that could be removed or not used | Input from Utilities on size/specification: Red -- critical to keep Yellow -- not functionally necessary but requires acceptance Green -- units that could be removed or not used Input from the Manufacturers: Understand what kind of volume that you see in these areas coupled with the number of variations that you experience. Two columns associated with each area that you can color code according to the picture at the right. Also feel free to add columns if there are other comments that you would like to provide.
Critical Design Specifications | There were several Options and Accessories which were identified that could pertain to several different transformer configurations. Some of these items were identified as potential add-on or Aftermarket installation options. The utilities were asked to color code responses in the Red/Yellow/Green format. There are still several questions with regard to Network transformer category as to what are custom specifications as opposed to options/accessories. | From utilities, the request was to color code the responses as: Red -- critical to keep Yellow -- not functionally necessary but requires acceptance Green -- units that could be removed or not used | Please provide input in the same Red/Yellow/Green format as described to the left for the importance of different options or accessories. We also ask for any comments/Concerns/Updates that you would like to share of the impact of utilizing or not, feasibility, impact, availability of materials, etc. that you see from the Manufacturing perspective.
Interchangeability Matrix | The tables presented represent the work in progress from utility input on areas critical components and available approved manufacturers that would be interchangeable or compatible either short term or long term for different transformer types. | This is a simple list outlining preferred vendor and alternate approved vendors for primary components. | It is expected that this list can be more comprehensive with input from Manufacturers to help identify areas for further interchangeability. Please fill in this table for critical components and vendors as they relate to the different transformer types. There are columns for comments or special requirements for further clarification.

## Taxonomy_Rev3
Design Attributes |  |  | Comments
| Impedance | Percentage, 85°C
| Total Ownership Cost (TOC) | DOE Efficiency Standards, A and B Factors | Guaranteed no-load losses and load losses
| Average Winding Temperature | 55°C, 65°C, 75°C, Dual Rating | High temperature insulating liquids
| Capacity Factor | kVA
| Physical Size/Weight | (Dimensions, mm), (Total weight, kg) | Including maximum footprint, Including all extruding accessories, Oil/No-Oil Weight
| Door Access | Multiple vs. single hinge | Position, dimensions
| Oil Capacity | Liters
Cable Entrance Openings
| Jack Bosses |  | Used on pads to insert fork lifts to move units around.
| Lifting Lugs/Provisions |  | Used for lifting pad mount transformers with rigging.
| Paint/Color | Pretreatment requirements, paint color | Specify pretreating the exterior before painting (after consulting with EPRI) and paint color. We use Munsel Green 7.0 GY3.29/1.5 for pads and ANSI 24 or 70 for OH tubs
| Nameplate material | Material Specifications | Stainless Steel, Anodized Aluminum, etc. Location and number of nameplates on 3ph padmounts
| Bracket Positions |  | IEEE specifies for OH transformers the spacing and configuration of pole mounting brackets.
| Basic Insulation Level Rating | 30kVA/45kV/60kV/75kV/95kV/110kV/125kV/150KV/200kV
| Application | Step-Up, Step-Down, etc.
| Losses | Core losses, copper losses
| Sound level | NEMA Standard, IEEE Std. C57.12.90
Windings/Coil
| Materials | Copper/Aluminum/Alloys
| Shape | Rnd/Strip
| AWG Size |  | Size of the winding conductors
| High Voltage/Low Voltage | Sizing requirements, I2R losses,
| Winding Configuration | Delta-Wye, Wye-Wye, etc. | Add phase displacement using IEEE standard naming convention (e.g. DYn1), Important in paralleling
Thermal Relay
| Phasing | Single phase, Three phase
Insulation system
| Solid Insulation Materials | Cellulose base, epoxy resin
| Mineral Oil | (inhibited/uninhibited)
| Ester Fluid | Natural/Synthetic
| Class 105 (A) | Materials or combinations of materials, which by experience or accepted tests, have been shown to give the required life at a continuous temperature of X°C.
Class 130 (B)
Class 155 (F)
Class 180 (H)
Class 220 (>H)
Class over-220
Transformer core
| Materials | Core losses, Form factor, | amorphous, silicon steel
Material Grade
| Core design | triplex, core type, shell type, 5-legged, Evans
Oil Tank/Housing
| Materials | Corrosion resistance, stainless steel | Free of PCB and corrosive Sulfur
| Temperature detector | Fluid temperature, winding temperature
| Pressure Relief device | PRV vs. alternate methods, IFD | May be designed to auto relief slow build up of internal transformer pressure.
| Fluid level indicator |  | Indicates internal transformer fluid level
| Tank pressure rating | Operating pressure rating and designed fail point to direct fluid downward in a vault | Might be known as high fault energy or safety tank design.
| Tank and Hardware Submersibility | Submersible or non-submersible design
| Sampling Valve | Location of sampling valve | Usually at the bottom of the transformer. May be opened to take an oil sample for analysis without creating hole in transformer.
| Seismic requirements | e.g. Moderate, High, etc.
Switches
| Load Tap Changer | A selector switch device, which may include current interrupting contactors, used to change transformer taps with the transformer energized and carrying full load. Syn: onload tap-changer (IEC 50). | Used to change the transformer turns ratios which can raise or lower the voltages. May be installed on primary or secondary side.
| De-energized Tap Changer | A selector switch device used to change transformer taps with the transformer de-energized. | Standard vs. Custom taps: Tap changer ((2) +/- 2.5% taps)
| Dual Voltage Switches | Standard ratios | Specialized ratios. Transformers may be used at different voltage levels. Useful to be installed on circuits with planned voltage conversions.
| 4 Position Switch | Used on loop fed, 3 ph transformers to de-energize transformer or turn off feeds (HXA or HXB) or have them all energized. | Two way (on-off) xfrmr switch is a SoCo Standard. Also, some of our xfrmrs have two-way LOOP-TIE switches.
2 - Position Switch
| 2 or 3 Position Network Switch | Primary dead-break or mag-break open, closed, ground positions. Safety interlock is required. Drain/sample valve required. | Used for operating on primary side of network transformers.
| 2 position LBOR switches |  | ON/OFF switch for three phase pad mounts
Cooling System
| Oil | Mineral Oil, (inhibited/uninhibited), Ester (natural/synthetic)
Dry
FM Approved
Radiator
| Cooling Classification | Natural/Forced/Liquid/Surfaces | e.g. ONAN/ONAF
Protection
Conventional vs. CSP
| Basic Impulse Level | 30kV/45kV/60kV/75kV/95kV/110kV/125kV/150KV/200kV
Bushing Class
| Arrestors | Internal vs. External | Arrestors under oil, Secondary Arrestor, Internal/External MOV
Transformer Comprehensive Management System (TCMS)
Terminals and Bushings
Bushing Well/Bushing Clamp/Bushing Insert
| Bushing Sizing | IEEE standard arrangement, per IEEE 386 interface | Specialized bushing arrangements. Primary bushing heights seem to vary greatly if not specified and secondary bushings should come with strain relief.
| Dead front | 200A Loadbreak | Could be a 600A T with bushing well. Dead front units would be specified with 200 A wells or 600 A bushing.
| Live front | 600/900A Deadbreak | Bushings are exposed
| Padmount Spade Bushings | Hole count 4-24, Universal spacing
| Single Phase | Studs | Clarification: the secondary bushings of 1ph xfrmrs are studs.
Grounding Tabs/Drain Wire
| Insulated Parking Bushing | Parking Stands for mounting | Use parking stands to mount the insulated parking bushings, the stands are provided with the transformer but not the bushings. Seen transformers with stand provisions for just a single feed and others with provisions for two feeds to be parked.
| Radial or Loop Fed |  | Padmounts can be radial (H1 1ph, H1, H2, H3 3ph) or loop fed (H1A, H1B, 1ph, H1A, H1B, H2A, H2B, H3A, H3B, 3ph)
| Bushing numbers |  | 1ph OH transformers can be 1 or 2 bushing design
| Neutral grounding |  | Generally, we specify the X2 bushing to be bonded with a ground strap to the tank on all transformers.
| Removable Ground connection between H0 and X0 |  | For pad mount 3ph wye-wye banks we require a switch that will open/close a connection between H0 and X0 for testing purposes. SoCo does not require a switch, but that the link is removable.
| Bushing Current Transformers (BCTs) | Accuracy class, thermal rating factor, multi-ratio, etc.
Fusing
| Current-limiting Type | A fuse that, when it is melted by a current within its specified current-limiting range, abruptly introduces a high arc voltage to reduce the current magnitude and duration.
| Expulsion Type | Expulsion fuses utilize gas and vapor mechanism to limit the duration of the current, but does not decrease its magnitude.
| Bayonet Style | Expulsion fuses that can be removed like a bayonet. Designed to remove most common electrical distribution system issues, such as overheating, overloading, secondary faults, and low level short circuits. Bayonets are removeable and load breaking
| Bushing Style | fuses mounted on the bushing
Terminal Board Style
| Isolation Link | A metal link that does not have an interrupting rating, but will melt to open the circuit during a transformer failure
| Fuse Cutout | External protection device with a fuse element that melts and isolates the circuit when current is exceeds a limit | Usually mounted overhead on poles or crossarms
| Protection curves | Graphical chart that shows the protection characteristic of the device | Used for protection coordination with other protection devices and operating conditions
Protection Limits
| Internal Fault Detection Sensor | May be part of pressure relief valve | Provides physical indication of internal fault (pops out a flag). Fault may also be sent to central command center remotely.
| Magnex Breaker |  | Used on 1ph pad mount transformers for protection. Is a Cooper only product as far as I know.
| Secondary Breaker |  | Used on OH CSP tubs.
| Dry Canister w/ NX fuses |  | Used on older models. Is a dry (IE fuse isn't oil embedded) and uses NX style fuses.

## Attributes_working_Utilities
Marking for items not included in original Tables | [8 empty] | No 3ph OH | No 3ph OH |  | Not use 3ph but 3 single phase in bank | [14 empty] | Do not use network Transformers
|  |  | 1P pole top | Utility 1 | Utility 2 | Utility 3 | Utility 4 | 3P pole top | Utility 1 | Utility 2 | Utility 3 | Utility 4 | 1P Pad | Utility 1 | Utility 2 | Utility 3 | Utility 4 | 3P pad | Utility 1 | Utility 2 | Utility 3 | Utility 4 | Network | Utility 1 | Utility 2 | Utility 3 | Utility 4 | 3P Vault/Submersible | Utility 1 | Utility 2 | Utility 3
|  |  | .5 (1440) |  |  |  |  | 10 (2340) |  |  |  |  | 10 (360) |  |  |  |  | 45 |  |  |  |  | 333 |  |  |  |  | 300
|  |  | 1 (1440) |  |  |  |  | 15 (2340) |  |  |  |  | 15 (360) |  |  |  |  | 75 |  |  |  |  | 500 |  |  | 3ph |  | 500
|  |  | 1.5 (1440) |  |  |  |  | 25 (2340) |  |  |  |  | 25 |  |  |  |  | 112.5 |  |  |  |  | 750 |  |  | 3ph |  | 750
|  |  | 3 (1440) |  |  |  |  | 37.5 (2340) |  |  |  |  | 37.5 |  |  |  |  | 150 |  |  |  |  | 1000 |  |  | 3ph |  | 1000
|  |  | 5 (1440) |  |  |  |  | 50 |  |  |  |  | 50 |  |  |  |  | 225 |  |  |  |  | 1500 |  |  | 3ph |  | 1500
|  |  | 10 (1440) |  |  |  |  | 75 |  |  |  |  | 75 |  |  |  |  | 250 |  |  |  |  | 2000 |  |  | 3ph |  | 2500
|  |  | 15 (1440) |  |  |  |  | 100 |  |  |  |  | 100 |  |  |  |  | 300 |  |  |  |  | 2500 |  |  | 3ph |  | 3325
|  |  | 25 (1440) |  |  |  |  | 167 |  |  |  |  | 167 |  |  |  |  | 500 |  |  |  |  | 100 (1ph) |  |  | 1ph
|  |  | 37.5 (1440) |  |  |  |  | 250 |  |  |  |  | 250 |  |  |  |  | 750 |  |  |  |  | 167 (1ph) |  |  | 1 ph |  | Submersible (1ph)
|  |  | 50 |  |  |  |  | 333 | [9 empty] | 1000 |  |  |  |  | 300 (3ph) |  |  | 1ph |  | 15
|  |  | 75 |  |  |  |  | 500 | [9 empty] | 1500 | [9 empty] | 25
|  |  | 100 |  |  |  |  | 750 | [9 empty] | 2000 | [9 empty] | 37.5
|  |  | 167 | [14 empty] | 2500 | [9 empty] | 50
|  |  | 250 | [14 empty] | 3000 | [9 empty] | 75
|  |  | 333 | [14 empty] | 3750 | [9 empty] | 100
|  |  | 500 | [14 empty] | 5000 | [9 empty] | 167
|  |  | 750 | [14 empty] | 7500 | [9 empty] | 250
3750
Protection
|  |  | 1P pole top | Utility 1 | Utility 2 | Utility 3 | Utility 4 | 3P pole top | Utility 1 | Utility 2 | Utility 3 | Utility 4 | 1P Pad | Utility 1 | Utility 2 | Utility 3 | Utility 4 | 3P pad | Utility 1 | Utility 2 | Utility 3 | Utility 4 | Network | Utility 1 | Utility 2 | Utility 3 | Utility 4
|  |  | Conventional |  |  |  |  | Conventional |  |  |  |  | Conventional |  |  |  |  | Conventional |  |  |  |  | Conventional
|  |  | Completely Self Protected |  |  |  |  | Completely Self Protected |  |  |  |  | FUSED |  |  |  |  | Fused/Fault Interrupter |  |  |  |  | Fused
| Bushing Class |  | 1P pole top* | Utility 1 | Utility 2 | Utility 3 | Utility 4
A
B-1
B-2
B-3
| BIL | 1P pole top/3P pole top/ 1P pad/ 3P pad/ Network | BIL rating | Utility 1 | Utility 2 | Utility 3 | Utility 4
|  | 2.4 | 45 |  |  | 45 | 45
|  | 4.16 | 60 |  | 60 | 60
|  | 4.8 |  |  |  | 60 | 60
|  | 6.9 |  |  | 60
|  | 7.2 | 75
|  | 7.62 |  |  |  | 75 | 75
7.97
8.32
|  | 12 | 95110 |  | 95
12.47
|  | 13.2 |  |  |  | 110 | 95
|  | 13.8 |  |  |  | 95/110 | 110
|  | 14.4 |  |  |  | 95/110
|  | 19.9 | 125150 |  |  | 125/150
|  | 22.86 |  |  |  |  | 125, 150
23
|  | 24.94 | 125150200 |  |  |  | 125, 150
|  | 20.8 |  |  | 125 |  | 200
|  | 34.5 |  |  |  | 150/200

## Attributes_working_Manufacturer
[6 empty] | Manufacturing Volume | Variations or SKU numbers | Manufacturing Volume | Variations or SKU numbers |  | Manufacturing Volume | Variations or SKU numbers | Manufacturing Volume | Variations or SKU numbers |  | Manufacturing Volume | Variations or SKU numbers | Manufacturing Volume | Variations or SKU numbers |  | Manufacturing Volume | Variations or SKU numbers | Manufacturing Volume | Variations or SKU numbers |  | Manufacturing Volume | Variations or SKU numbers | Manufacturing Volume | Variations or SKU numbers
|  | Marking for items not included in original Tables |  |  |  | MFG 1 | MFG 1 | MFG 2 | MFG 2 | Corrected kVA below | MFG 1 | MFG 1 | MFG 2 | MFG 2 |  | MFG 1 | MFG 1 | MFG 2 | MFG 2 |  | MFG 1 | MFG 1 | MFG 2 | MFG 2 |  | MFG 1 | MFG 1 | MFG 2 | MFG 2 |  | Manufacturing Volume | Variations or SKU numbers
Input of Interest |  |  |  | kVA Rating | 1P pole top |  |  |  |  | 3P pole top |  |  |  |  | 1P Pad |  |  |  |  | 3P pad |  |  |  |  | Network |  |  |  |  | 3P Vault/Submersible
Manufacturing Volume | High |  |  |  | .5 (1440) |  |  |  |  | 45 |  |  |  |  | 10 (360) |  |  |  |  | 45 |  |  |  |  | 333 |  |  |  |  | 300
| Medium |  |  |  | 1 (1440) |  |  |  |  | 75 |  |  |  |  | 15 (360) |  |  |  |  | 75 |  |  |  |  | 500 |  |  |  |  | 500
| Low |  |  |  | 1.5 (1440) |  |  |  |  | 112.5 |  |  |  |  | 25 |  |  |  |  | 112.5 |  |  |  |  | 750 |  |  |  |  | 750
| N/A |  |  |  | 3 (1440) |  |  |  |  | 150 |  |  |  |  | 37.5 |  |  |  |  | 150 |  |  |  |  | 1000 |  |  |  |  | 1000
Variations or SKU numbers | High |  |  |  | 5 (1440) |  |  |  |  | 225 |  |  |  |  | 50 |  |  |  |  | 225 |  |  |  |  | 1500 |  |  |  |  | 1500
| Medium |  |  |  | 10 (1440) |  |  |  |  | 250 |  |  |  |  | 75 |  |  |  |  | 250 |  |  |  |  | 2000 |  |  |  |  | 2500
| Low |  |  |  | 15 (1440) |  |  |  |  | 300 |  |  |  |  | 100 |  |  |  |  | 300 |  |  |  |  | 2500 |  |  |  |  | 3325
| N/A |  |  |  | 25 (1440) |  |  |  |  | 500 |  |  |  |  | 167 |  |  |  |  | 500 |  |  |  |  | 100 (1ph)
[5 empty] | 37.5 (1440) |  |  |  |  | 167 |  |  |  |  | 250 |  |  |  |  | 750 |  |  |  |  | 167 (1ph) |  |  |  |  | Submersible (1ph)
[5 empty] | 50 | [14 empty] | 1000 |  |  |  |  | 300 (3ph) |  |  |  |  | 15
[5 empty] | 75 | [14 empty] | 1500 | [9 empty] | 25
[5 empty] | 100 | [14 empty] | 2000 | [9 empty] | 37.5
[5 empty] | 167 | [14 empty] | 2500 | [9 empty] | 50
[5 empty] | 250 | [14 empty] | 3000 | [9 empty] | 75
[5 empty] | 333 | [14 empty] | 3750 | [9 empty] | 100
[5 empty] | 500 | [14 empty] | 5000 | [9 empty] | 167
[5 empty] | 750 | [14 empty] | 7500 | [9 empty] | 250
3750
Protection
[5 empty] | 1P pole top |  |  |  |  | 3P pole top |  |  |  |  | 1P Pad |  |  |  |  | 3P pad |  |  |  |  | Network
[5 empty] | Conventional |  |  |  |  | Conventional |  |  |  |  | Conventional |  |  |  |  | Conventional |  |  |  |  | Conventional
[5 empty] | Completely Self Protected |  |  |  |  | Completely Self Protected |  |  |  |  | FUSED |  |  |  |  | Fused/Fault Interrupter |  |  |  |  | Fused
|  |  | Bushing Class |  | 1P pole top* | Not sure what this is.
A
B-1
B-2
B-3
|  |  | BIL | 1P pole top/3P pole top/ 1P pad/ 3P pad/ Network | BIL rating
|  |  |  | 2.4 | 45
|  |  |  | 4.16 | 60
4.8
6.9
|  |  |  | 7.2 | 75
7.62
7.97
8.32
|  |  |  | 12 | 95110
12.47
13.2
13.8
14.4
|  |  |  | 19.9 | 125150
22.86
23
|  |  |  | 24.94 | 125150200
20.8
34.5

## Critical Specifications_Input
Classification by Color
Red – option/accessory to keep​
Yellow – option/accessory not functionally necessary but will require an organizational acceptance​
Green – option/accessory can be removed​
Overhead transformer options and accessories
Option or Accessory​ | Potential for “Aftermarket Installation”​ | Comments/Concerns/Updates
Taps either two 2.5% above and below; four 2.5% below, NEMA taps or special taps​ | No​
Externally operable tap changer switches for safe operation​ | No​
High corrosion area protection with 304 or 409 stainless steel hardware and tanks​ | No​
MagneX™ interrupter​ | No​
Birdguards​ | Yes​
Envirotemp™ FR3™ fluid where less-flammable fluid is required, and superior environmental characteristics are desired​ | Yes​
Cover with a minimum dielectric strength of 15 kV​ | No​
Extra creep high voltage bushings (up to 150 kV BIL)​ | No​
Porcelain low-voltage bushings​ | No​
Canadian Standards Association (CSA) conforming design​ | No​
Special designs conforming to international specifications​ | No​
Drain/sampling valve​ | Yes​
Pressure vacuum gauge (tank size limitations apply)​ | Yes​
Filter press connections​ | No​
Temperature gauge (tank size limitations apply)​ | Yes​
Liquid level gauge (tank size limitations apply)​ | Yes​
High efficiency transformers at 0.05% or higher above DOE efficiency​ | No​
Secondary breaker with weak link for secondary fault and overload protection​ | No​
Primary weak link fuse​ | No​
Current limiting fuse for high interrupting ratings and limiting fault currents​ | No​
Low-voltage distribution class MOV arrester – internally or externally mounted​ | No​
Lightning arresters for primary over-voltage protection: direct connected, normal or heavy duty metal oxide varistor (MOV) internal​ | No​
Lightning arresters for primary over-voltage protection: direct connected, normal or heavy duty metal oxide varistor (MOV) external​ | Yes​
High voltage bushing location - cover mounted or side wall mounted​ | No​
Dual voltage switch​ | No​
Stainless steel tank​ | No​
Primary Termination – cover mounted or side wall mounted​ | No​
Secondary Termination – Porcelain vs. polymer bushings​ | No​
Primary Switching – externally operated tap changer, dual voltage switch or terminal board​ | Yes​
Overcurrent Protection – internally mounted current limiting fuse in series with protective link​ | Yes​
Pad mounted transformer options and accessories​
Option or Accessory​ | Potential for “Aftermarket Installation”​
Various multiple voltages or taps​ | No​
Externally-operable multiple voltage or tap changer switches for safe operation​ | No​
Stainless steel tank, tank bottom, sill, door, and/or hardware​ | No​
Service entrance in sill​ | No​
Various spades and terminals available for secondary bushings​ | Yes​
High efficiency transformers at 0.05% above DOE efficiency or higher​ | No​
Stenciled bushing designations​ | No​
High-voltage bushing inserts​ | No​
Ground connectors​ | Yes​
Captive stainless steel hexhead door locking bolt​ | Yes​
RUS design​ | No​
One piece high-voltage bushings​ | No​
High-voltage bushing wells with removable studs​ | No​
Envirotemp™ FR3™ fluid​ | Yes​
Canadian Standards Association (CSA) and Consumer Electronics Association (CEA) designs​ | No​
Special designs to meet international specifications​ | No​
Load break switches​ | No​
Drain/sampling valve​ | Yes​
Pressure vacuum gauge​ | Yes​
Liquid level gauge1​ | Yes​
Temperature gauge1​ | Yes​
Combination shipping and installation poly-pad​ | No​
Network transformer options and accessories​
Option or Accessory​ | Potential for “Aftermarket Installation”​
Series-multiple high-voltage winding​ | No​
Delta-wye connection​ | No​
Special high-voltage taps​ | No​
Special low-loss high efficiency designs​ | No​
Design optimization to lowest total owning cost​ | No​
50 Hertz operating frequency​ | No​
Special impedance​ | No​
Special sound level​ | No​
Special phase relationship​ | No​
Special BIL level​ | No​
Over excitation capability​ | No​
65° C average temperature rise​ | No​
Special ambient temperature​ | No​
Operation at altitudes above 3300 feet​ | No​
Core ground test point located inside tank accessible from bolted handhole​ | No​
Electrostatic shields​ | No​
Optional tank features and accessories​ | --​
Special hardware​ | No​
Welded handhole cover​ | No​
Additional bolted or welded hand-hole​ | No​
Special tank design pressure (up to 15 psig)​ | No​
Ground connectors​ | Yes​
Special tank dimensions​ | No​
Tank undercoating​ | No​
Omit pressure-relief valve​ | No​
Optional gauges and fittings​ | --​
Dial-type magnetic liquid-level gauge (with alarm contacts)​ | No​
Dial-type thermometer (with alarm contacts)​ | No​
Pressure-vacuum gauge (with or without alarm contacts)​ | No​
Automatic pressure-relief device (with or without alarm contacts)​ | No​
Drain valve with liquid sampling valve​ | Yes​
Additional drain valve on tank or switch chamber​ | Yes​
Spare gaskets​ | Yes​
Sight gauge for high-voltage terminal chamber​ | Yes​
Option or Accessory​ | Potential for “Aftermarket Installation”​
Optional high-voltage entrance features and accessories​ | --​
Single-conductor or multi-conductor wiping sleeves, or pothead entrance​ | No​
Six universal bushing wells for loop feed with or without loadbreak inserts​ | No​
Three integral loadbreak bushings​ | No​
Three non-Ioadbreak bushings​ | No​
Six non-Ioadbreak bushings for loop feed​ | No​
Optional low-voltage air terminations​ | --​
Welded low-voltage bushings​ | No​
Fully insulated low-voltage neutral bushing​ | No​
Other low-voltage termination options​ | No​
Optional network protector provisions (check with factory)​ | No​
Optional dielectric fluids​ | --​
Silicone fluid​ | No​
FR3 natural ester-based fluid​ | No​
Option or Accessory​ | Potential for “Aftermarket Installation”​
Optional high-voltage switch features and accessories​ | --​
Interrupting switch or other special switches​ | No​
Provisions for phase sequence identification​ | No​
Phase sequence indication​ | No​
Additional electrical interlocks​ | No​
Viewing windows for observation of switch blades​ | No​

## Interchangeability Matrix_Input
Transformer |  |  |  | Approved Manufacturer |  | Approved Manufacturer |  | Approved Manufacturer |  | Approved Manufacturer |  | Approved Manufacturer |  | Approved Manufacturer |  | Approved Manufacturer |  | Substitution Status |  | Specific Vendor Requirements
Type: | Size | Primary Component | Category | Manufacturer | Model # | Manufacturer | Model # | Manufacturer | Model # | Manufacturer | Model # | Manufacturer | Model # | Manufacturer | Model # | Manufacturer | Model # | Short Term Only | Long Term | Performance | Quality | Other | Aftermarket Option
OH, 1Ph, etc. | kVA | Fuse, Sticker, MOV | Protection, Marking | [14 empty] | Only to expedite | Completely interchangeble | Critical matching requirements | Test specs or other metrics |  | Ability to add at Utility